ADDENDUM-II

M/s. Enviro Control Associates(I) Pvt. Ltd., Surat.

| Sr. No | Queries | Answers |
| --- | --- | --- |
| 1. | Please refer Vol.1, Chapter 1, IT-10 c, Page No.21. We request you to consider submission of tender documents into the separate sealed cover by way of speed post or Hand Delivery as per your tenser condition for 10 MLD Water Treatment Plant. | The Bidder may submit the tender documents in separate sealed cover by way of Speed Post or Hand Delivery. |
| 2. | Please refer the eligibility criteria, Page No. 13 of Vol.1. We understand that in absence of similar nature of works for SBR / MBR technology. The applicant must have tie-up with a technology provider as per NIT condition. Please Confirm. | Please refer Addendum – 1. |
| 3. | We understand that pre-qualification criteria in alternative bid offer based on MBR technology shall be as per clause IT-10, Page 21 of Vol.1. Please confirm. | Confirmed |
| 4. | Please refer Chapter-1, Clause 2, Page 15,16 of Vol.I – Evaluation Criteria. You are kindly requested to review %age variance allowance of 12 to 15% in case of O & M cost. As far as guarantee concern, we feel that there should not be more than + 1% variance allowed and if it exceeds then guaranteed value, penalty must be applicable during O & M period. | The variation upto 3% shall be allowed during O&M period for guaranteed power and chemical consumptions given by the Bidder in their offer. |
| 5. | Please refer Chapter-1, Clause 1.1.6.1, Page 3 of Vol.II. The GA drawings / RCC drawings shall be submitted during detailed engineering after award of work. Only layout & hydraulic flow diagram shall be submitted alongwith filled-up tender. Please confirm. | Confirmed |
| 6. | The minimum grade of concrete shall be M30 for all liquid retaining structures and M20 for all buildings and other structures. The PCC shall be minimum 100 mm thick for concrete grade M10 for buildings and water retaining structures. Please confirm. | Confirmed |

| 7. | We suggest to consider following minimum thickness shall be used for different RCC members irrespective design thickness. Please confirm. Sr.No; Civil Member; Width (mm). 1; Walls for liquid retaining structures; 200. 2; Base Slab of liquid retaining structures; 200. 3; Wall foundation (at junction of base slab & wall) of liquid retaining structures; 300. 4; Roof Slab of liquid retaining structures; 150. 5; Walls of launders; 150. 6; Base slab of launders; 125. 7; Floor slabs including roof slabs, walkways canopy slabs; 100. 8; Walls of cables / pipe trenches, underground pits, etc.; 125. 9; Footing – Edge thickness; 200. 10; Footing – At the face of column; 450. 11; Column; 230 (width) 300 (depth). 12; Parapets, chajja; 100. 13; Pre cast trench cover; 75. 14; Beam; 230 (width) 300 (depth). | Agreed |
| --- | --- | --- |
| 8. | Please confirm the ground water table for design of water retaining structure as Chapter-4, Clause 1.3 of Vol.I shows the GWT as 2 Mtr. whereas Chapter-1, Clause 1.1.2, Page 2 of Vol.II shows GWT as 3.0 Mtr. below from existing ground level. | The Bidder shall consider Ground Water Table at 3.0 M below existing Ground Level. |
| 9. | Please confirm the length and size of HDPE pipeline to be laid by the bidder from GHB’s end upto inlet chamber of MPS unit for costing purpose. | The Supply and Laying of 900 mm dia HDPE pipes up to the Battery Limit of STP premises shall be in GHB’s scope. However, contractor shall have to carry out the work of laying and jointing of HDPE Pipes up to the Inlet Chamber of Main Pumping Station as per the approved layout. |
| 10. | Please refer Chapter-2, Clause 1.3.1.3, Page 7 of Vol.II shows 2 Nos. (1 mechanical + 1 manual standby) of screens for MPS units whereas Clause 1.3.2.1, Page 9 of Vol.II shows 3 Nos. (2 W+ 1S )of screens. Please confirm the exact requirement for the said item. | The Contractor shall provide 2 Nos. (1 W Mechanical + 1 Manual Stand-by) of Screens for Main Pumping Station units. The specifications shall be as per Addendum-1. |

| 11. | You are also requested to provide the detailed specifications of screens required for MPS units. | Please refer Addendum-1. |
| --- | --- | --- |
| 12. | The tender does not specify area required for RCC Chlorine Toner Shed, RCC Centrifuge Shed as well as Chlorination Room with RCC frame brick masonry structures. Therefore, you are requested to provide the minimum specific area required for the said units. | The area required for Chlorination Room including toner provision shall be of minimum 40 sq.m. and Centrifuge shed shall be of minimum 100 sq.m. area. Rooms shall be in RCC frame Brick Masonary structures. |
| 13. | Please refer Chapter-2, Clause 1.4.2 & 1.4.3, Page 12-13 of Vol.II. We suggest to provide One manual fine screen and manual grit channel as standby unit for Sewage Treatment Plant. | The Bidder shall provide One Manual Fine Screen and Manual Grit Channel for STP. |
| 14. | All chemicals require to operate and maintain the Sewage Treatment Plant shall be provided by GHB during O & M period. Please confirm. | Confirmed |
| 15. | We suggest to provide 2 Nos. of Aluminum Sluice Gates at inlet of treated sewage collection sump for operational flexibility during O & M period. | The treated sewage collection sump shall be provided without partition wall and hence provision of sluice gates are not required. |
| 16. | We suggest to provide minimum 150 cum volume of RCC UF feed tank with 3 Nos. (2W+1S) of 45.83 M3/hr. capacity each submersible type UF Feed Pump. | Agreed |
| 17. | The treated permeate from UF system shall be taken to treated sewage collection sump by permeate pumps of 3 Nos.(2W+1S) having capacity of 41.66 M3/hr.each. Please confirm. | Confirmed |
| 18. | Please refer Chapter 2, Clause 1.4.7, Page 18 of Vol.2. The treated sewage collection sump shall be provided with RCC cover. Please confirm. | Confirmed |

HNB ENGINEERS PVT. LTD

| Sr. No | Queries | Answers |
| --- | --- | --- |
| 1. | Please provide Layout and Hydraulic Flow Diagram for STP site. | The Bidder has to provide Layout Plan and Hydraulic Flow Diagram drawings based on his design for STP site as EPC Contract. |
| 2. | Please advice on supply of construction Power, water supply and supply points within the selected plot. | Please refer Clause No.G.C. – 03, Page-37, Scope of Work, Tender Volume-I. Developer shall bear all monthly electrical consumption charges during trial run & operation & maintenance period. |
| 3. | Please provide the length and diameter on incoming HDPE Pipes to the inlet of Main Pumping Station. | The Supply and Laying of 900 mm dia HDPE pipes up to the Battery Limit of STP premises shall be in GHB’s scope. However, contractor shall have to carry out the work of laying and jointing of HDPE Pipes up to the Inlet Chamber of Main Pumping Station as per the approved layout. |
| 4. | Kindly advice on scope of work of Chemicals and Electricity during commissioning, trial run and O&M period. | All chemicals and electricity during Trial Run, Commissioning and O&M period shall be provided by GHB. |
| 5. | We presume that client will provide the clear site in award of work. | Confirmed |
| 6. | Please confirm the diffuser arrangement requirement in SBR tank, whether it is fixed or retrievable? | The Diffuser arrangement required in SBR Tank shall be fixed type non-retrievable. |
| 7. | No DG requirement is mentioned in the tender, how to manage power at the time of power failure? please clarify. | GHB shall provide electricity during Trial Run and O&M period and hence DG is not required and hence not in the scope of Bidder. |
| 8. | The MS Pipes shall be as per IS:3589 (DN200 and above size). Please confirm. | The MS Pipes shall be as per latest relevant IS Standards. |
| 9. | We request you to make 5% interest free advance payment to facilitate us to mobilize our resources against bank guarantee. | GHB shall provide interest free advance of 10% of the total contract value initially towards mobilization against bank guarantee for equivalent amount. This shall be recovered @20% of monthly R.A.Bills. |
| 10. | If in case of termination of contract, we request you to pay the balance amount to the contractor within 15-days from the date of termination. | Confirmed |
| 11. | We assume that in Main Pumping Station, the screen chamber shall have coarse screen (I Mechanical + 1 stand-by Manual). The clear opening between the bars shall be 20 mm and shall be of MS epoxy painted. The screenings from the mechanical screen shall be collected mechanically atleast 2 M above plinth level. The screen shell be provided with raking arrangement, conveyor belt and chute arrangement. | Please refer Addendum-I for MOC of screens for MPS. However, we agreed that the screenings from the mechanical screen shall be collected mechanically atleast 2 M above plinth level. The screen shall be provided with raking arrangement, conveyor belt and chute arrangement. |

| 12. | We suggest that CI Sluice Gates shall be provided at the upstream and downstream of the each screen channel to isolate the flow in Main Pimping Station and hand wheel and actuator shall be provided I M FGL for ease in operation. Further, minimum clear height of pump shall be 4.5 M. Please confirm. | Confirmed |
| --- | --- | --- |
| 13. | Please clarify the scope of final treated sewage transfer pumps with number, capacity and its head. | The Bidder has to provide 3 Nos. of Final Treated Sewage Transfer Pumps, Submersible Type having 104.16 M3/hr capacity each with minimum 15 M Head. |
| 14. | As Per page-16, Evaluation Criteria un Volume-1, the guaranteed power and chemical consumption shall not exceed 12-15% As per standard professional practice, there shell not be any variation allowed as it may mislead evaluation of the life cycle cost of STP and finally lost to the users in future. | The variation up to 3% shall be allowed during O&M period for guaranteed power and chemical consumptions given by the Bidder in their offer. |
| 15. | Please confirm water level of wet sump in Main pimping station with minimum Side Water Depth. | The maximum water level of the Wet Sump in MPS shall be 44.80 RL with minimum of 2 M Side Water Depth. |

GHARPURE ENGINEERING AND CONSTRUCTIONS (P) LTD.

| Sr. No. | Queries | Answer |
| --- | --- | --- |
| 1 | We have designed and executed SBR technology based plants in India and we qualify our own the tender per-qualifying criteria and therefore, assume that necessarily tie-up with the technology provider is not required. | The Bidder must have necessarily tie-up with Technology Provider. Please refer Addendum-1. |
| 2 | The eligibility criteria for MBR technology is differed to that of indicated in NIT, Volume-1, Page-14 and Page-21. Please clarify. | Please refer Addendum-1. |
| 3 | We assume that excess excavated earth should be disposed off within the STP plot and if it has to be disposed off the other site, and then the charges for the same shall be paid extra. | The excess excavated earth shall be disposed off within STP & Solid Waste Management plots (No. 26 & 27) to develop FGL. |
| 4 | We assume that battery limit for dewatered sludge shall be at bottom of centrifuge. Further storing/handling/disposal shall be taken care by the developer. | Confirmed |
| 5 | Generally, such contracts provide interest free advance payment initially towards mobilization limited to 10% of the total contract value against bank guarantees of equivalent amount. This helps to mobilize the site faster and to maintain the case flow. Please provide the same and confirm. | GHB shall provide interest free advance of 10% of the total contract value initially towards mobilization against bank guarantee for equivalent amount. This advance shall be recovered @20% of monthly R.A.Bills. |
| 6 | Please provide us the mechanical specifications of manual screen to be installed at upstream of wet well. | Please refer Addendum-1. |
| 7 | There shall be dedicated dosing pumps to each centrifuge. We presume that there should be 2 Nos. (1 W+ 1S) pumps. Please confirm. | Confirmed |
| 8 | The centrifuge shall be with SS 304 wetted parts. Kindly confirm. | Please refer Addendum-1. |
| 9 | Please clarify the minimum area for sludge dewatering building and also confirm the number of centrifuge to be installed including future provision if applicable. | The Centrifuge Building shall be of 100 sq.m. area minimum including dosing facility. |
| 10 | Please provide the mechanical specifications of Belt Conveyor for Main Pumping Station and STP. | Please refer Addendum-1. |
| 11 | Pleas specify the scope of water, electricity and chemicals during trial run. | GHB shall provide water, electricity and chemicals during trial run, testing and commissioning as well as O&M period . |
| 12 | We request you to consider provision of storage tank at upstream side of Ultra Filtration System for smooth operation of UF during O&M. | The Bidder shall provide 150 M3 of Liquid Volume for UF Feed Tank of RCC M30 concrete with 3 Nos. (2 W + 1 S) of 45.83 M3/hr capacity each of submersible type UF Feed Pumps with suitable head. |
| 13 | The tenderer shall be quote electrical, mechanical and instrument items as well civil works including cement, steel and other basic materials without Excise Duty. VAT, CST and Service Tax. Please reconfirm. | Confirmed |